SPECIFICATIONS FOR

SCREW PILE FOUNDATIONS

<EDIT: YOUR JOB NAME HERE>

1. GENERAL

  - Purpose of Specification

The purpose of this specification is to detail the furnishing of all materials, tools, equipment, labor supervision, and installation techniques necessary to install screw piles as detailed on the drawings, including connection details.  This shall include provisions for load testing that may be part of the scope of work.

  - Scope of Work

This work consists of furnishing all necessary, supervision, labor, tools, materials, and equipment to perform all work necessary to install the screw piles, at <YOUR JOB NAME HERE> for the <OWNER NAME HERE> per the specifications described herein, and as shown on the drawings.  The Contractor shall install a HPM that will develop the load capacities as detailed on the drawings.

  - Qualifications of the Screw Pile Contractor

The screw pile Contractor shall be experienced in the installation of screw pile foundations and shall furnish all materials, labor, and supervision to perform the work.  The Contractor shall provide names of on-site personnel materially involved with the work, including those who carry documented certification of screw pile training.  At a minimum, these personnel shall include foreman, machine operator, and project engineer/manager.

The screw pile Contractor shall not sublet the whole or any part of the contract without the express written permission of the Owner.

  - Definitions

A partial list follows.  The Owner may wish to add other specific, project-related items.

Design Load (DL):	Maximum anticipated service load applied to the screw anchor.  Also known as the working load (WL).

Helical Extension:	Screw pile component installed immediately following the lead section, if required.  This component consists of one or more helix plates welded to a central steel shaft of finite length.

HELICAL PULLDOWN™ Micropile:	A small diameter, soil displacement, cast-in-place screw pile.  Load transfer to soil is both end bearing and friction.  United States Patent 5,707,180, Method and Apparatus for Forming Piles In-Situ. A.k.a. HPM.

Helix Plate:	Generally round steel plate formed into a ramped spiral.  The helical shape provides the means to install the helical tieback anchor, plus the plate transfers load to soil in end-bearing.  Helix plates are available in various diameters and thicknesses.

Lead Section:	The first screw pile component installed into the soil, consisting of single or multiple helix plates welded to a central steel shaft.  Helix plates provide end-bearing capacity.

Plain Extension:	Central steel shaft of finite length without helix plates.  It is installed following the installation of the lead section or helical extension (if used).  The units are connected with integral couplings and bolts.  Plain extensions are used to extend the helix plates beyond the specified minimum depth and into competent load bearing stratum.

Safety Factor:	The ratio of the ultimate capacity to the working or design load of the screw pile.

Working Load (WL):	Equivalent term for Design Load.

Ultimate Capacity (UC):	Limit state based on the structural and/or geotechnical capacity of the ground anchor defined as the point at which no additional capacity can be justified.

  - Allowable Tolerances

    - Centerline of screw pile shall not be more than 3 inches from indicated plan location.

    - Screw pile plumbness shall be within 2 of design alignment.

    - Top elevation of screw pile shall be within +1 inch to –2 inches of the design vertical elevation.

  - Quality Assurance

    - The Contractor shall employ an adequate number of skilled workers who are experienced in the necessary crafts and who are familiar with the specified requirements and methods needed for proper performance of the work of this specification.

    - All screw piles shall be installed in the presence of a designated representative of the Owner unless said representative informs the Contractor otherwise.  The designated representative shall have the right to access any and all field installation records and test reports.

    - Screw pile components as specified therein shall be manufactured by a facility whose quality systems comply with ISO (International Organization of Standards) 9001 requirements.  Certificates of Registration denoting ISO Standards Number shall be presented upon request to the Owner or their representative.

  - Ground Conditions

The Geotechnical Report, including logs of soil borings as shown on the boring location plan, shall be considered to be representative of the in-situ subsurface conditions likely to be encountered on the project site.  Said Geotechnical Report shall be used as the basis for screw pile foundation design using generally accepted engineering judgment and methods.

- REFERENCED CODES AND STANDARDS

Standards listed by reference, including revisions by issuing authority, form a part of this specification section to the extent indicated.  Standards listed are identified by issuing authority, authority abbreviation, designation number, title, or other designation established by issuing authority.  Standards subsequently referenced herein are referred to by issuing authority abbreviation and standard designation.  In case of conflict, the particular requirements of this specification shall prevail.  The latest publication as of the issue of this specification shall govern, unless indicated otherwise.

  - American Society for Testing and Materials (ASTM):

    - ASTM A29/A29M Steel Bars, Carbon and Alloy, Hot-Wrought and Cold Finished.

    - ASTM A36/A36M Structural Steel.

    - ASTM A53 Pipe, Steel, Black and Hot-Dipped, Zinc-Coated Welded and Seamless.

    - ASTM A153 Zinc Coating (Hot Dip) on Iron and Steel Hardware.

    - ASTM A252 Welded and Seamless Steel Pipe Piles.

    - ASTM A775 Electrostatic Epoxy Coating

    - ASTM A193/A193M Alloy-Steel and Stainless Steel Bolting Materials for High Temperature Service.

    - ASTM A320/A320M Alloy-Steel Bolting Materials for Low Temperature Service.

    - ASTM A500 Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes.

    - ASTM A572 HSLA Columbium-Vanadium Steels of Structural Quality.

    - ASTM A618 Hot-Formed Welded and Seamless High-Strength Low-Alloy Structural Tubing.

    - ASTM A656 Hot-Rolled Structural Steel, High-Strength Low-Alloy Plate with Improved Formability.

    - ASTM A1018 Steel, Sheet and Strip, Heavy Thickness Coils, Hot Rolled, Carbon, Structural, High-Strength Low-Alloy, Columbium or Vanadium, and High-Strength Low-Alloy with Improved Formability.

    - ASTM D1143 Method of Testing Piles Under Static Axial Compressive Load.

    - ASTM D3689 Method of Testing Individual Piles Under Static Axial Tensile Load.

  - American Welding Society (AWS):

    - AWS D1.1 Structural Welding Code – Steel.

    - AWS D1.2 Structural Welding Code – Reinforcing Steel.

  - American Society of Civil Engineers (ASCE):

    - ASCE 20-96 Standard Guidelines for the Design and Installation of Pile Foundations.

  - Deep Foundations Institute (DFI):

    - Guide to Drafting a Specification for High Capacity Drilled and Grouted Micropiles for Structural Support, 1st Edition, Copyright 2001 by the Deep Foundation Institute (DFI).

  - Post Tensioning Institute (PTI):

    - Recommendations for Prestressed Rock and Soil Anchors, Third Edition, Copyright 1996 By the Post-Tensioning Institute.

  - Society of Automotive Engineers (SAE):

    - SAE J429 Mechanical and Material Requirements for Externally Threaded Fasteners.

- SUBMITTALS

  - Construction Submittals

    - The Contractor shall submit a detailed description of the construction procedures proposed for use to the Owner for review.  This shall include a list of major equipment to be used.

    - The technical submittal shall include the following:

      - Screw pile number, location and pattern by assigned identification number if not indicated on plans

      - Load required of each screw pile

      - Type and size of central steel shaft

      - Helix configuration (number and diameter of helix plates proposed)

      - Minimum effective installation torque

      - Minimum depth

      - Minimum cased length, if applicable.

      - Grout column diameter

      - Technical data for grout material

      - Means for mixing and placing grout

      - Screw pile attachment to structure relative to grade beam, column pad, pile cap, etc.

    - The Contractor shall submit shop drawings for all screw pile components, including corrosion protection and pile top attachment to the Owner for review and approval. This includes screw pile lead and extension section identification (manufacturer’s catalog numbers).

    - Work shall not begin until all the submittals have been received and approved by the Owner.

  - Installation Records

The Contractor shall provide the Owner copies of screw pile installation records within 24 hours after each installation is completed.  Formal copies shall be submitted on a weekly basis.  These installation records shall include, but are not limited to, the following information.

    - Name of project and Contractor

    - Name of Contractor’s supervisor during installation

    - Date and time of installation

    - Name and model of installation equipment

    - Type of torque indicator used

    - Location of screw pile by assigned identification number

    - Actual central steel shaft type and configuration – including lead section (number and size of helix plates), number and type of extension sections

    - Screw pile installation duration and observations

    - Total length of installed screw pile

    - Cut-off elevation

    - Inclination

    - Installation torque at one-foot intervals for the entire length

    - Grout quantities pulled-down on a per section basis

    - Actual grout column diameter and length

    - Comments pertaining to interruptions, obstructions, rate of advancement or other relevant information

- PRODUCTS AND MATERIALS

  - Central Steel Shaft:

The central steel shaft, consisting of lead sections, helical extensions, and plain extensions, shall be <Material Type Here – Solid Square Shaft, Pipe Shaft etc. > Type <XYZ Here> as manufactured by A.B. Chance or approved equal.

    - Solid Square Shaft Material (1.5”x1.5”):  Shall be hot rolled Round-Cornered-Square (RCS) solid steel bars meeting dimensional and workmanship requirements of ASTM A29.  The bar shall be modified medium carbon steel grade (similar to AISI 1044) with improved strength due to fine grain size.

      - Torsional strength rating = 5,500 ft-lb

      - Minimum yield strength = 70 ksi

    - Solid Square Shaft Material (1.5”x1.5”):  Shall be hot rolled Round-Cornered-Square (RCS) solid steel bars meeting the dimensional and workmanship requirements of ASTM A29.  The bar shall be High Strength Low Alloy (HSLA), low to medium carbon steel grade with improved strength due to fine grain size.

      - Torsional strength rating = 7,000 ft-lb

      - Minimum yield strength = 90 ksi

    - Solid Square Shaft Material (1.75”x1.75”):  Shall be hot rolled Round-Cornered-Square (RCS) solid steel bars meeting the dimensional and workmanship requirements of ASTM A29.  The bar shall be High Strength Low Alloy (HSLA), low to medium carbon steel grade with improved strength due to fine grain size.

      - Torsional strength rating:  = 11,000 ft-lb

      - Minimum yield strength = 90 ksi

    - Solid Square Shaft Material (2.0”x2.0”):  Shall be hot rolled Round-Cornered-Square (RCS) solid steel bars meeting the dimensional and workmanship requirements of ASTM A29.  The bar shall be High Strength Low Alloy (HSLA), low to medium carbon steel grade with improved strength due to fine grain size.

      - Torsional strength rating:  = 16,000 ft-lb

      - Minimum yield strength = 90 ksi

    - Solid Square Shaft Material (2.25”x2.25”):  Shall be hot rolled Round-Cornered-Square (RCS) solid steel bars meeting the dimensional and workmanship requirements of ASTM A29.  The bar shall be High Strength Low Alloy (HSLA), low to medium carbon steel grade with improved strength due to fine grain size.

      - Torsional strength rating:  = 23,000 ft-lb

      - Minimum yield strength = 90 ksi

    - Pipe Shaft Material (2.875” O.D.):  Shall be structural steel tube or pipe, seamless or straight-seam welded, per ASTM A500 Grade B.  Wall thickness is 0.203” (schedule 40).

      - Torsional strength rating = 5,500 ft-lb

      - Minimum yield strength = 50 ksi

    - Pipe Shaft Material (2.875” O.D.):  Shall be structural steel tube or pipe, seamless or straight-seam welded, per ASTM A500 Grade B.  Wall thickness is 0.276” (schedule 80).

      - Torsional strength rating = 8,000 ft-lb

      - Minimum yield strength = 50 ksi

    - Pipe Shaft Material (3.5” O.D.):  Shall be structural steel tube or pipe, seamless or straight-seam welded, ASTM A53, A252, A500, or A618.  Wall thickness is 0.300” (schedule 80).

      - Torsional strength rating = 13,000 ft-lb

      - Minimum yield strength = 50 ksi

  - Helix Bearing Plate:

Helix plates material shall be hot rolled carbon steel sheet, strip, or plate formed on matching metal dies to true helical shape and uniform pitch.  Bearing plate material shall conform to the following ASTM specifications.

    - Solid Square Shaft Material (Torque ≤ 5,500 ft-lb): Per ASTM A572, or A1018, or A656 with minimum yield strength of 50 ksi.  Plate thickness is 3/8”.

    - Solid Square Shaft Material (Torque ≥ 5,500 ft-lb): Hot rolled steel sheet, strip or plate per ASTM A656 or A936 with minimum yield strength of 80 ksi. Plate thickness is 3/8” or 1/2”.

    - Pipe Shaft Material (Torque ≤ 5,500 ft-lb.): Hot Rolled carbon steel, strip, or plate per ASTM A568 with minimum yield strength of 50 ksi.  Alternate materials are A-36 or ASTM A572 Grade 50.  Plate thickness is 3/8”.

    - Pipe Shaft Material (Torque ≥ 5,500 ft-lb.): Per ASTM A36, or A572, or A1018, or A656 depending on helix diameter, with minimum yield strength of 80 ksi.  Plate thickness is 3/8” or 1/2”.

  - Bolts:

The size and type of bolts used to connect the central steel shaft sections together shall conform to the following ASTM specifications.

    - Solid Square Shaft Material (Torque ≤ 7,000 ft-lb): 3/4” diameter bolt per ASTM A320 Grade L7.

    - Solid Square Shaft Material (Torque ≥ 7,000 ft-lb): 7/8” – 1-1/4” per ASTM A193 Grade B7

    - Pipe Shaft Material (Torque ≤ 13,000 ft-lb): ¾” diameter bolts (# of bolts per coupling depends on torque) per SAEJ429 Grade 5.

  - SAE J429 Grade 5:  Sy (min) = 92 ksi, Su (min) = 120 ksi

  - Couplings:

Couplings shall be capable of transmitting both the maximum installation torque from the tool string to the helix plates, and the maximum axial load from the top of the pile to the helical bearing plates.

  - Plates, Shapes, or Pier Caps:

Structural steel plates and shapes for screw pile top attachments shall conform to ASTM A36 or ASTM A572 Grade 50.

  - Pipe/Casing:

If steel casing is relied upon to carry compression or lateral loads, or to stiffen the HPM, the casing/pipe shall conform to the ASTM specifications as cited in paragraph 4.7.1.  If PVC casing is relied upon for grout containment, fissured or void-filled soils, or as a bond breaker, the casing/pipe shall conform to the  ASTM specifications as cited in paragraph 4.7.2.

    - Shall meet or exceed the physical and general requirements of ASTM A53 Type E or S Grade B, A252 Grade 2, A500 Grade B, or ASTM A618.

    - Shall meet the physical and general requirements of ASTM D1784, D1785, and D3034.

  - Water

Water for mixing grout shall be potable, clean and free from impurities, which may be detrimental to grout or steel.  Potable water shall be available in quantities sufficient to mix grout and for equipment clean-up.

  - Cement

Cement for HELICAL PULLDOWN™ Micropile grout shall be Portland cement conforming to ASTM C150 Type I or Type II.  Pre-packaged, non-shrink cement grouts shall be subject to the review and acceptance of the Owner, and shall conform to the requirements of ASTM C1107.

  - Admixtures

Chemical admixtures for grout shall conform to the requirements of ASTM C494.  Chemical admixtures which control bleed water, improve consistency, reduce water/cement ratio, and retard set may be used in the grout subject to the review and acceptance of the Owner.  Expansive admixtures can be used to fill confined areas of the central steel shaft coupling joints, or to compensate for drying shrinkage.  Accelerators shall not be permitted.  Chemical admixtures, if used, shall be compatible with the central steel shaft and mixed in accordance with the grout manufacturer’s recommendations.

Mineral admixtures for grout shall conform to the requirements of ASTM C618 (coal fly ash) or C1240 (silica fume).  Mineral admixtures, which provide thixotropic consistency, reduce porosity, increase compressive strength, and resist segregation may be used in the grout subject to the review and acceptance of the Owner.  Mineral admixtures, if used, shall be compatible with the central steel shaft and mixed in accordance with the grout manufacturer’s recommendations.

Grout specimen testing is generally not required for production piles, but is required for pre-production tests to evaluate the quality and strength of the grout mix.  If required, a strength test shall be the average of the strength of two specimens made from the same sample of grout as used for production HPMs and tested at 28 days or at the test age designated for determination of compressive strength.  The specimens shall be made and cured under field conditions in accordance with ASTM C31 and tested in accordance with ASTM C39.

  - Aggregate

Sand fillers may be used in the grout mix as an extender with large diameter grout columns, subject to the approval of the Owner.  Use fine sand only.  Medium or coarse sand shall not be permitted.  Small diameter grout columns shall not include aggregate.

  - Corrosion Protection

    - Galvanization:  All screw pile material that is not encased in grout or concrete shall be hot-dipped galvanized in accordance with ASTM A153 after fabrication.

- EXECUTION

  - Site Conditions

    - Prior to commencing screw pile installation, the Contractor shall inspect the work of all other trades and verify that all said work is completed to the point where screw pile installation may commence without restriction.

    - The Contractor shall verify that all screw piles may be installed in accordance with all pertinent codes and regulations regarding such items as underground obstructions, right-of-way limitations, utilities, etc.

    - In the event of a discrepancy, the Contractor shall notify the Owner.  The Contractor shall not proceed with screw pile installation in areas of discrepancies until said discrepancies have been resolved.

  - Installation Equipment

    - Shall be rotary type, hydraulic power driven torque motor with clockwise and counter-clockwise rotation capabilities.  The torque motor shall be capable of continuous adjustment to revolutions per minute (RPM’s) during installation.  Percussion drilling equipment shall not be permitted.  The torque motor shall have torque capacity 15% greater than the torsional strength rating of the central steel shaft to be installed.

    - Equipment shall be capable of applying adequate down pressure (crowd) and torque simultaneously to suit project soil conditions and load requirements.  The equipment shall be capable of continuous position adjustment and swing capacity at maximum installation torque to maintain proper screw pile alignment during installation.  The application of bending stress to the pile during installation will not be permitted.

  - Installation Tooling

    - Shall consist of a Kelly Bar Adapter (KBA) and drive tool as appropriate for the central shaft of the screw pile under maximum installation torque and used in accordance with the manufacturers written installation instructions.

    - Installation tooling should be maintained in good working order and safe to operate at all times.  Flange bolts and nuts should be regularly inspected for proper tightening torque. Bolts, connecting pins, and retainers should be periodically inspected for wear and/or damage and replaced with identical items provided by the manufacturer.  Heed all warning labels.  Worn or damaged tooling should be replaced.

    - A torque indicator shall be used during screw pile installation.  The torque indicator shall be a device that directly measures torque and that is mounted in-line with the installation tooling.  Devices that infer torque from hydraulic pressure will not be permitted.

      - Shall be capable of providing continuous measurement of applied torque throughout the installation.

      - Shall be capable of torque measurements in increments of 200 ft-lb or less.

      - Shall be re-calibrated, if in the opinion of the Owner and/or Contractor reasonable doubt exists as to the accuracy of the torque measurements.

  - Installation Procedures

    - Central Steel Shaft:

      - The screw pile installation technique shall be such that it is consistent with the geotechnical, logistical, environmental, and load carrying conditions of the project.

      - The lead section shall be positioned at the location as shown on the working drawings.  Battered screw piles can be positioned perpendicular to the ground to assist in initial advancement into the soil before the required batter angle shall be established.  The screw pile sections shall be engaged and advanced into the soil in a smooth, continuous manner at a rate of rotation of not to exceed 16 RPM’s.  The extension sections shall be provided to obtain the required minimum overall length and installation torque as shown on the working drawings.  Connect sections together using coupling bolt(s) and nut torqued to 40 ft-lb.

      - Sufficient down pressure shall be applied to uniformly advance the screw pile sections approximately 3 inches per revolution.  The rate of rotation and magnitude of down pressure shall be adjusted for different soil conditions and depths.

      - A lead displacement plate (LDP) of appropriate diameter shall be positioned on the central steel shaft at the location necessary to install the grout column as shown on the working drawings.  The LDP shall not be located closer than 12 inches above the top helical plate.  Additional LDP’s or extension displacement plates (EDP) shall be positioned on the central steel shaft at regular intervals – typically at every coupling joint.  Displacement plates shall not be spaced more than 7-ft. apart.  Displacement plates shall permit the free flow of grout without misalignment of the central steel shaft.

    - Grout:

      - Grout shall be mixed with equipment capable of providing a steady supply at the required level of production.  When using a pre-packaged grout, the recommended water-cement ratios listed in the mixing instructions on the package shall be followed.

      - The grout shall be placed via a gravity fed reservoir located at the surface.  The reservoir shall consist of a temporary casing or form, which is capable of containing liquid grout.  The reservoir shall be appropriately sized (diameter and length) to accommodate the soil conditions and grout column diameter.  The grout shall be placed in reservoir immediately prior to the advancement of the first LDP into the soil.  The volume of grout contained in the reservoir shall be maintained at a level sufficient to maintain positive hydrostatic pressure on the grout column.

      - Grout placement shall continue until the minimum grout column length has been achieved as shown on the working drawings.  Volume measurements shall be taken throughout the installation in order to determine the actual grout column diameter.

      - Grout shall be allowed to attain the minimum design strength prior to being loaded.

    - Casing:

      - If required, casing shall be installed in segments corresponding to the sections of the central steel shaft.

      - The casing shall be advanced into the soil via direct connection with lead and extension displacement plates.

      - Each casing segment shall be filled with grout immediately after placement.

  - Termination Criteria

    - The torque as measured during the installation shall not exceed the torsional strength rating of the central steel shaft.

    - The minimum installation torque and minimum overall length criteria as shown on the technical submittal shall be satisfied prior to terminating the screw pile foundation installation.

    - If the torsional strength rating of the central steel shaft and has been reached prior to achieving the minimum overall length required, the Contractor shall have the following options:

      - Terminate the installation at the depth obtained subject to the review and acceptance of the Owner, or:

      - Remove the existing screw pile and install a new one with fewer and/or smaller diameter helix plates.  The new helix configuration shall be subject to review and acceptance of the Owner.

    - If the minimum installation torque as shown on the working drawings is not achieved at the minimum overall length, and there is no maximum length constraint, the Contractor shall have the following options:

      - Install the screw pile deeper using additional extension sections, or:

      - Remove the existing screw pile and install a new one with additional and/or larger diameter helix plates.

      - De-rate the load capacity of the screw pile and install additional helical screw foundation(s).  The de-rated capacity and additional helical screw foundation location shall be subject to the review and acceptance of the Owner.

    - If the screw pile is refused or deflected by a subsurface obstruction, the installation shall be terminated and the pile removed.  The obstruction shall be removed, if feasible, and the screw pile re-installed.  If the obstruction can’t be removed, the screw pile shall be installed at an adjacent location, subject to review and acceptance of the Owner.

    - If the torsional strength rating of the central steel shaft and has been reached prior to proper positioning of the last plain extension section relative to the final elevation, the Contractor may remove the last plain extension and replace it with a shorter length extension.  If it is not feasible to remove the last plain extension, the Contractor may cut said extension shaft to the correct elevation.  The Contractor shall not reverse (back-out) the screw pile to facilitate extension removal.

    - The average torque for the last three feet of penetration shall be used as the basis of comparison with the minimum installation torque as shown on the working drawings.  The average torque shall be defined as the average of the last three readings recorded at one-foot intervals.

- LOAD TESTS

  - Pre-Production Pile Tests (Optional)

Load tests shall be performed to verify the suitability and capacity of the proposed HELICAL PULLDOWN™ Micropile, and the proposed installation procedures prior to installation of production piles.  ___________ sacrificial test piles with reaction anchors shall be constructed immediately prior to the start of work on the production HPMs.  The Owner shall determine the number of pre-production test piles, their location, acceptable load and movement criteria, and the type(s) of load direction (i.e., tension, compression, or both).  Additional purpose of pre-production tests is to empirically verify the ultimate capacity to the average installing torque of the screw pier foundation for the project site.

Pre-production pile installation methods, procedures, equipment, and overall length shall be identical to the production piles to the extent practical except where approved otherwise by the Owner.

The Contractor shall submit for review and acceptance the proposed HPM load testing procedure.  The pre-production test proposal shall be in general conformance with ASTM D1143 and/or D-3689, and shall provide the minimum following information:

- Type and accuracy of load equipment

- Type and accuracy of load measuring equipment

- Type and accuracy of pile-head deflection equipment

- General description of load reaction system, including description of reaction anchors

- Calibration report for complete load equipment, including hydraulic jack, pump, pressure gauge, hoses, and fittings.

If the pre-production test fails to meet the design requirements, the Contractor shall modify the HPM design and/or installation methods and retest the modified pile, as directed by the Owner.

  - Load Test Procedures

The hydraulic jack shall be positioned at the beginning of the test such that the unloading and repositioning of the jack during the test shall not be required.  The jack shall also be positioned co-axial with respect to the pile-head so as to minimize eccentric loading.  The hydraulic jack shall be capable of applying a load not less than two times the proposed design load (DL).

An alignment load (AL) shall be applied to the HPM prior to setting the deflection measuring equipment to zero or a reference position.  The AL shall be no more than 10% of the design load (i.e., 0.1 DL).  After AL is applied, the test set-up shall be inspected carefully to ensure it is safe to proceed.

Axial pile load tests shall be conducted by loading the HPM in step-wise fashion as shown in Table-3 to the extent practical.  Pile-head deflection shall be recorded at the beginning of each step and after the end of the hold time.  The beginning of the hold time shall be defined as the moment when the load equipment achieves the required load step.

Test loads shall be applied until continuous jacking is required to maintain the load step or until the test load increment equals 200% of the design load (DL) (i.e., 2.0 DL), whichever occurs first.  The observation period for this last load increment shall be 10 minutes.  Displacement readings shall be recorded at 1, 2, 3, 4, 5 and 10 minutes (load increment maxima only).

The applied test load shall be removed in four approximately equal decrements per the schedule in Table-3.  The hold time for these load decrements shall be 1 minute, except for the last decrement, which shall be held for 5 minutes.

Table-3. Steps for Pre-Production Load Testing

| LOAD STEP | HOLD TIME (MINUTES) |
| --- | --- |
| 0 | 2.5 Min. |
| 0.25 DL | 2.5 Min. |
| 0.50 DL | 2.5 Min. |
| 0.750 DL | 2.5 Min. |
| DL | 10.0 Min. |
| 0.75 DL | 1.0 Min. |
| 0.50 DL 0.25 DL | 1.0 Min. 1.0 Min. |
| 0 | 1.0 Min. |
| 0.25 DL | 1.0 Min. |
| 0.50 DL | 1.0 Min. |
| 0.75 DL | 1.0 Min. |
| DL | 1.0 Min. |
| 1.25 DL | 2.5 Min. |
| 1.50 DL | 2.5 Min. |
| 1.75 DL | 2.5 Min. |
| 2.0 DL | 10.0 Min. |
| 1.5 DL 1.0 DL 0.5 DL 0 | 2.5 Min. 2.5 Min 2.5 Min 5.0 Min |

AL = Alignment Load; DL = Design Load

  - Production Pile Testing

(This may be the only type of load test conducted, depending on project conditions.)

The Contractor shall perform proof tests on a minimum of ___% of the total production HPMs.  The piles to be tested will be selected by the Owner.  At the Contractor’s suggestion, but with the Owner’s permission, tension tests may be performed in lieu of compression tests up to 1.00 DL for HPMs with sufficient structural tension capacity.  The requirements of Table-4 may be regarded as a minimum, however, it is not recommended to test production piles to values of up to 2.0 DL unless the pile’s failure load is significantly higher than 2.0 DL.  The maximum production pile test load shall be determined by the Owner.  For example, ASTM D1143 stipulates testing to 2.0 DL.

The test sequence shall be as shown in Table-4 to the extent practical.

Table-4. Steps for Production Load Testing

| LOAD STEP | HOLD TIME (MINUTES) |
| --- | --- |
| AL | 0 Min. |
| 0.20 DL | 2.5 Min. |
| 0.40 DL | 2.5 Min. |
| 0.60 DL | 2.5 Min. |
| 0.80 DL | 2.5 Min. |
| 1.00 DL | 5 Min. |
| 0.60 DL | 1 Min. |
| 0.40 DL | 1 Min. |
| 0.20 DL | 1 Min. |
| AL | 5 Min. |

AL = Alignment Load; DL = Design Load

The acceptance criteria for production piles shall be per Section 6.3 Item 1.

If a production HPM that is tested fails to meet the acceptance criteria, the Contractor shall be directed to proof test another HPM in the vicinity.  For failed piles and further construction of other piles, the Contractor shall modify the design, the construction procedure, or both. These modifications include, but are not limited to, installing replacement HPMs, modifying the installation methods and equipment, increasing or decreasing the grout column diameter, increasing the minimum effective installation torque, changing the helix configuration, increasing the grout column length, or changing the HPM material (i.e., central steel shaft, grout mix, etc.).  Modifications that require changes to the structure shall have prior review and acceptance of the Owner.

END OF SPECIFICATION

APPENDIX

TABLE-1

A. B. CHANCE COMPANY

MECHANICAL STRENGTH RATINGS – HELICAL SCREW PILES

| RATING TYPE | CENTRAL STEEL SHAFT FAMILY |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | SS5 1-1/2” RCS | SS150 1-1/2” RCS | SS175 1-3/4” RCS | SS200 2” RCS | SS225 2-1/4” RCS |
| Torsional Strength Rating (ft-lb) | 5,500 | 7,000 | 11,000 | 16,000 | 23,000 |
| Ultimate Capacity Per Helix (kip) (Tension/Compression) | *40 | *40 | *50 | 60 | 60 |
| Minimum Ultimate Tension Capacity (kip) (Connection Limit) | 70 | 70 | 100 | 150 | 200 |
| Dywidag Thread Bar Diameter2 (inch) | 1 | 1 | 1 | 1 & 1-1/4 | 1-1/4 & 1-3/8 |

* For 14” Dia. Helix Plates, Reduce the Ultimate Capacity by 20%

- Actual installed capacities are dependent on existing soil conditions.

- Thread bar tendons shall have a minimum guaranteed ultimate tensile strength of 150 ksi.  Tendons shall meet the requirements of ASTM A722-Grade 150.  Steel anchorage nuts and bearing plates shall be compatible with the specified tendons.